## spec
Priority | Location | Parameter | Mechanism | Frequency | Notes | Initial investigation (week Jul. 13) | Aquasight / Inframark / Both? | Comments
1 | Forecast | 5 Day Forecast | NOAA / Local News | 1 minute
1 | Forecast | Precipitation | NOAA NWS API | 1-minute
2 | Forecast | Wind Speed | NOAA NWS API | Hourly
2 | Forecast | Wind Direction | NOAA NWS API | Hourly
1 | Forecast | Tide Stage (Predicted) | NOAA CO-OPS API | 6-minute | Station 8422687
2 | Forecast | Storm Surge | NOAA CO-OPS API | 6-minute
| Forecast | Wave Height | NOAA NWS API | Hourly
2 | Forecast | Coastal Flood Advisory | NWS Alerts API | Event-driven | MAZ015 zone filter
| Forecast | Hurricane/Tropical Storm Watch | NWS Alerts API | Event-driven | MAZ015 zone filter
2 | Rainfall | Precipitation Intensity | NOAA API | 1-minute | Nearest obs. station; do we add our own gauge?
2 | Rainfall | Precipitation Accumulation | NOAA API | 1-minute | Storm total since event start
1 | Rainfall | Radar Imagery | NOAA RIDGE API | 5-minute | Visual embed
2 | Pump Station (each) | Wet Well Level | SCADA | 1-minute |  | Yes
2 | Pump Station (each) | Wet Well Level Trend | Calculated | Derived | Rate of change on level signal
1 | Pump Station (each) | Influent Flow Rate | SCADA | 1-minute |  | Yes
2 | Pump Station (each) | Pump Runtime | SCADA | 1-minute |  | Yes
1 | Pump Station (each) | Pump Status (On/Off/Alarm) | SCADA | 1-minute |  | Yes
| Pump Station (each) | Cycle Frequency | Calculated | Derived | Pump cycles per hour; I/I proxy
| Pump station (each) | Total pump starts per day | SCADA | Derived | Pump starts per day | Yes
| Pump station (each) | Total pump starts per day alarm | SCADA | Alarm | Alarm if we exceed or are below expected starts (Client request) | Yes
1 | Pump station and WWTF | All alarms | SCADA | Alarm | Any pre-programmed alarms (Client request) | Yes
1 | Plant Influent | Flow Rate | Flow Meter (SCADA) | 1-minute
1 | Plant Influent | Influent Gate % Open Status | SCADA | 1-minute |  | Yes
1 | Plant Influent | Pump(s) Status | SCADA | 1-minute | Influent pump status | Yes
2 | Plant Influent | Flow Rate (% of Capacity) | Calculated | Derived
| Plant Influent | Conductivity | Conductivity Meter (SCADA) | 1-minute | We committed to add this to the influent in the RFP | Yes
2 | Plant Influent | Saltwater Intrusion Flag | Calculated | Derived | Threshold-based; conductivity proxy for surge
1 | Plant Effluent | Flow Rate | Flow Meter (SCADA) | 1-minute
1 | Plant Effluent | Pump(s) Status | SCADA | 1-minute | Effluent pump status (high tide situations?) | Yes
2 | Plant Effluent | CCT Level and Alarm (effluent discharge) | SCADA (or WIMS?) | 1-minute | Client request | Yes
2 | Aeration | Blower Status (On/Off/Alarm) | SCADA | 1-minute |  | Yes
| Aeration | Blower Runtime | SCADA | 1-minute |  | Yes
| Aeration | Air Flow Rate | SCADA | 1-minute |  | Yes
| Aeration | DO | SCADA | 1-minute | Online DO probes in aeration basins (not sure if these exist?) | Yes
1 | Disinfection | Chlorine / SBS | WIMS (or SCADA if dosing is integrated) | Hourly | Dose rate, residual, inventory on-hand | Yes
| Bypass/Overflow | Bypass Valve Position | SCADA | 1-minute |  | Yes
| Bypass/Overflow | Bypass Flow Rate | Flow Meter (SCADA) | 1-minute
| Bypass/Overflow | Bypass Active Flag | Calculated | Derived | Binary indicator
| Bypass/Overflow | Bypass Duration | Calculated | Derived | Regulatory reporting support
| Bypass/Overflow | Bypass Volume (Cumulative) | Calculated | Derived | Regulatory reporting support
1 | Kallipr Units | Kallipr Data | Edge device? | 1-minute |  | Yes
2 | Pump Stations / Plants | Rain Guage Data | SCADA | 1-minute | Client request | Yes
1 | Interceptor (all) | Level & Transducer | SCADA | 1-minute | Client request | Yes
1 | D Street Stormwater PS | Bay Water Level | SCADA | 1-minute | Client request | Yes
| Pump Station (each) | Pump Selection & Runtime Advisor ($/MG by combo) | WaterMinds ML model | Derived | APOLLO — recommends lowest-cost pump combination in real time ¦ Hull — delivered/documented (Milestone 2)
| Pump Station (each) | Pump Health & Efficiency (Actual vs Design %) | Calculated | Derived | APOLLO — degradation/efficiency-gap tracking, beyond the on/off/alarm status already in spec ¦ Hull — delivered/documented (Milestone 2)
| Aeration | Smart O2 / Oxygen Feed Advisor | WaterMinds ML model | 1-minute | APOLLO — DO setpoint optimization vs actual air supplied, $ gap tracking ¦ Hull — delivered/documented (Milestone 3)
| Secondary Clarification | Blanket Depth | WIMS | Daily | APOLLO — new process area, not currently in spec; needed to support RAS/WAS advisors below ¦ Hull — supporting data for delivered RAS/WAS advisors (Milestone 3) | Yes
| Secondary Clarification | RAS Pumping Advisor (state point analysis) | WaterMinds ML model | 1-minute | APOLLO — new process area, not currently in spec ¦ Hull — delivered/documented (Milestone 3)
| Secondary Clarification | WAS Advisor (MCRT-based) | WaterMinds ML model | Derived | APOLLO — new process area, not currently in spec ¦ Hull — recommended to Hull in Milestone 3, not yet shown as fully running
| Solids Handling | Sludge %TS (thickener out vs hauled) | WIMS / SCADA | Daily | APOLLO — new process area, not currently in spec at all ¦ Hull — delivered/documented (Milestone 5) | Yes
| Solids Handling | Polymer Feed / Solids Disposal Advisor | WaterMinds ML model | Derived | APOLLO — hauling cost & truck-count optimization ¦ Hull — delivered/documented (Milestone 5)
| Collection System | I&I Decomposition by Node (BSF / Infiltration / Inflow) | WaterMinds ML model | Daily | APOLLO — splits flow into components; current spec only has raw interceptor level ¦ Hull — delivered/documented (Milestone 4, ongoing in Q4 2023 report)
| Collection System | Node Design Capacity % & Overload Alert | Calculated | 1-minute | APOLLO — % utilization vs design capacity per node, not currently in spec ¦ Hull — delivered/documented (Milestone 4)
| Collection System | Automated Monthly I&I Report (RDII, RDII Ratio, GWI, Peaking Factor, Recovery Time, Rain Intensity) | WaterMinds reporting | Monthly | APOLLO — standardized, regulatory-ready I&I report; replaces manual compilation ¦ Hull — proposed in 2025 upgrade scope, not yet delivered
| Reporting | Quarterly Seasonal Performance Summary (YoY) | WaterMinds reporting | Quarterly | APOLLO — mirrors Aquasight's Q4 client summary deliverable ¦ Hull — this IS the Q4 2023 Summary deliverable, already in production
| Reporting | Cost/Savings Tracking ($/MG, O&M savings identified vs. realized, capital leverage) | Calculated | Monthly | APOLLO — savings tracking dashboard, mirrors Aquasight's savings tables ¦ Hull — delivered/documented (final report Tables 1-5b)
| Plant-wide | AI Assistant (Q&A, image analysis, SOP retention) | WaterMinds AI Assistant | On-demand | APOLLO — note: Aquasight's own AVA does NOT connect to live client data; decide if ours should be wired into live data or knowledge-only ¦ Hull — proposed in 2025 upgrade scope (AVA), not yet delivered
| WaterMinds Portal | Client Org Setup (Hull) | WaterMinds Admin | One-time | Provision Hull as a client org in WaterMinds
| WaterMinds Portal | User Accounts & Role-Based Access | WaterMinds Admin | One-time, then as-needed | Grant Hull staff logins; access expands as each feature above rolls out
| Project Magic (ML Compliance) | Seasonal Operating Range Model | WaterMinds ML Compliance Engine | Quarterly or Monthly — TBD | Statistically sets seasonal operating ranges from plant performance vs. regulatory limits; need to decide cadence
| Project Magic (ML Compliance) | Compliance Limit Comparison / Exceedance Flagging | WaterMinds ML Compliance Engine | Same cadence as above | Flags parameters trending outside ML-set range before a limit is actually breached
| Project Magic (ML Compliance) | Model Retrain / Refresh | WaterMinds ML Compliance Engine | Quarterly or Monthly — TBD | Re-runs against updated WIMS/SCADA history each cycle
Note on B37: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bypass?
Note on C45: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Bay Water Level

## apollo gap assessment
Apollo Capability | Process Area | Status | What We Already Have | What's Missing (if any) | How Apollo Proposes Doing It | Stated Intent / Value | Evidenced for Hull? | Evidence Recency (Hull items only)
Real-Time Data Treatment (live SCADA monitoring) | Plant-wide | Full Overlap | Spec pulls SCADA on 1-min intervals across pump stations, influent, effluent, aeration, bypass | — | Polls SCADA historian (Proficy, via OLE DB drivers) plus WIMS lab data on a set interval (their Hull build: 20-sec poll, 1-min rate) | Give ops a live, capital-free view of the plant that complements — not replaces — SCADA automated control | Hull — delivered/documented | Confirmed active — shown in Q4 2023 report (Jan 2024) (the underlying platform had to be live to produce that report)
Live Unit Process Dashboards | Plant-wide | Full Overlap | Dashboard already organized by unit process (pump stations, influent, effluent, aeration, disinfection, bypass) | — | Same underlying data feed, organized into per-process screens | Remote/control-room visibility for performance status, audit, and review, viewable outside the SCADA network without VPN | Hull — delivered/documented | Confirmed active — shown in Q4 2023 report (Jan 2024) (same — platform was live to produce that report)
Weather Optimized Influent Pumping / Influent Flow & Pollutant Forecast | Plant Influent | Partial Overlap | We already pull weather/tide forecast (Forecast section) and raw influent flow | The ML model tying weather/tide to a predicted influent flow & pollutant load | They describe it generally as combining real-time process data, lab data, weather/tide forecasts, and 'AI models' — no specific algorithm named. In practice at Hull this showed up as a cost-baseline/heuristic model (dry vs. wet weather $/MG by pump combo), not a disclosed forecasting model | Let ops pre-position pumping ahead of a storm/tide event and avoid running expensive pump combos unnecessarily | GLWA case study only — not confirmed for Hull | n/a — see 'Evidenced for Hull?' column
Digital Asset Intelligence / Pump Health & Efficiency Advisor | Pump Station / Effluent Pumping | Partial Overlap | Pump status, runtime, starts/day, alarms | Actual-vs-design efficiency %, degradation cost tracking | Compares actual $/MG and actual efficiency against the pump's original design curve (rated flow/head/speed at 60Hz); % efficiency gap = (actual eff − design eff) / design eff; savings modeled by assuming restoration to 90% of the original curve | Quantify what pump wear is costing in $/yr and prioritize which pumps justify R&R spend, ranked by runtime-weighted payback | Hull — delivered/documented (underlying capability shown in Hull Milestone 2; 'Digital Asset Intelligence' is the GLWA case study's name for it) | Confirmed active — shown in Q4 2023 report (Jan 2024) (Q4 2023 Table 3 shows efficiency % per pump combo)
Pump Selection & Runtime Cost Advisor ($/MG by combo) | Pump Station (each) | Partial Overlap | Pump status/runtime data feeding into it | The cost-per-combination calc and recommendation logic | Computes a weighted average $/MG for every pump/combo actually run, then flags cheaper combos (e.g., single large pump vs. two small pumps) and recommends shifting the runtime ratio toward the cheaper one | Capture savings with zero capex — pure operational/setpoint change, no equipment investment required | Hull — delivered/documented | Confirmed active — shown in Q4 2023 report (Jan 2024) (Q4 2023 Table 3 shows $/MG per pump combo directly)
Effluent Analysis | Plant Effluent | Partial Overlap | Raw effluent flow rate and pump status | Efficiency/degradation tracking on effluent pumps | Same actual-vs-design $/MG and efficiency-gap approach used on influent pumps, applied to the effluent station | Identify degradation-driven cost on the effluent side, same logic as influent | Hull — delivered/documented (underlying capability shown in Hull Milestone 2; 'Effluent Analysis' is the GLWA case study's name for it) | Confirmed active — shown in Q4 2023 report (Jan 2024) (Q4 2023 Table 3 includes Effluent PS stats)
SAMI 24x7 Autonomous Monitoring (anomaly detection) | Plant-wide | Partial Overlap | Pre-programmed alarms on pump starts/day and other client-requested triggers | ML-based detection of unprogrammed deviations from normal pattern | Compares real-time flow against the expected dry-weather-flow (ADWF) trend; flags deviations that aren't explained by rain or tide. Their proof point: caught a stuck PVC pipe in a check valve at PS-3 because gpm drifted off-pattern with no corresponding weather driver | Catch equipment problems (stuck valves, sensor drift, etc.) before they become bigger failures — a 'digital buddy' watching between site visits | GLWA case study only — not confirmed for Hull (Hull's PS-3 anomaly catch shows similar behavior informally, but 'SAMI' isn't named or confirmed in any Hull doc) | n/a — see 'Evidenced for Hull?' column
Oxygen Feed Advisor & Nitrification Index | Aeration | Partial Overlap | Blower status/runtime, air flow rate, DO (if probes exist) | The optimization advisor comparing actual air supplied vs. Apollo's recommended setpoint | Compares actual blower cost/kW against an 'Apollo advised' cost/kW under continuous vs. intermittent run schemes, by time of day/season; the gap between actual and advised (e.g., -33% in one month) sizes the savings and informs a right-sizing (smaller blower) recommendation | Trim air supply to what the biology actually needs — flagged as a strong candidate for energy-grant funding too | Hull — delivered/documented (Smart O2 advisor is in Hull Milestone 3 with real data; 'Nitrification Index' specifically is not mentioned in any Hull doc) | Delivered in 2020 pilot — no confirmation of continued use since
Disinfection Dosage Advisor | Disinfection | Partial Overlap | Raw chlorine/SBS dose rate, residual, inventory (via WIMS) | The dosing optimization advisor | Not detailed for Hull specifically (Hull's milestones don't cover disinfection) — description is the same general 'real-time + lab + AI model' smart-advise approach used elsewhere | Minimize chemical (hypochlorite/bisulfite) use while still meeting or beating permit limits | GLWA case study only — not confirmed for Hull | n/a — see 'Evidenced for Hull?' column
Collection System Intelligence (I&I by node) | Collection System | Partial Overlap | Raw interceptor level/transducer data | BSF / Infiltration / Inflow decomposition, GIS node map, design-capacity % alerts | Splits each node's flow into Base Sanitary Flow (from dry-weather flow analysis), Infiltration, and Inflow (from rainfall/tide-correlated flow response above the dry baseline); GIS map shows live gpm and cumulative gph per node with design-capacity alerts; a 'Decode' view gives 7-day raw flow overlaid with weather | Pinpoint which nodes/months drive I&I so rehab dollars target the worst offenders — their model showed 50% I&I reduction would cut plant capacity utilization from 74% to 54% and save ~$84K/yr | Hull — delivered/documented | Confirmed active — shown in Q4 2023 report (Jan 2024) (Q4 2023 Table 1 & 2 are this exact output, by node)
SOP Knowledge Retention | Plant-wide | Net New | — | No knowledge-capture/training-retention feature in spec | Framed as a 'secondary objective' of the platform — SOPs live in the system, and (per the AVA feature) staff can query them conversationally instead of digging through binders | Preserve institutional knowledge as experienced operators retire/turn over, and speed up onboarding of new staff | Hull — delivered/documented (boilerplate platform description appears in Hull's own final report, but not built out as a dedicated Hull feature/milestone) | Delivered in 2020 pilot — no confirmation of continued use since (was always a general description, not a demonstrated feature)
Chemical-P Removal Advisor | Chemical Feed | Net New | — | No phosphorus removal optimization in spec | Not detailed for Hull (no chemical P removal process there) — same general real-time + lab + AI 'smart advise' framing as the other advisors | Hit phosphorus permit limits with minimum chemical spend | GLWA case study only — not confirmed for Hull (Hull's process doesn't even include phosphorus removal) | n/a — see 'Evidenced for Hull?' column
RAS Pumping Intelligence (state point analysis) | Secondary Clarification | Net New | — | Secondary Clarification isn't a covered process area at all | Uses State Point Analysis (a clarifier settleability method) against the clarifier's design operating curve plus SVI/MLSS data to find the minimum safe RAS rate; recommends stepping RAS down incrementally (e.g. .9→.7 MGD, eventually toward .4) while watching blanket depth and nitrification as guardrails, and deliberately uses conservative (overestimated) SVI/MLSS inputs so it doesn't over-recommend | $4,507/yr (17.4%) energy savings — another no-capex, pure-setpoint win, but one that needs a settleability safety margin built in | Hull — delivered/documented | Delivered in 2020 pilot — no confirmation of continued use since
WAS Advisor (MCRT-based) | Secondary Clarification | Net New | — | Same — process area not covered | Real-time Mean Cell Residence Time (MCRT/SRT) calculation used to recommend a WAS pumping rate/schedule, including an intermittent-WAS option | Keep sludge age dialed to target without a manual daily calc | Hull — delivered/documented (recommended to Hull in Milestone 3 text, presented as a next step rather than something already running) | Delivered in 2020 pilot — no confirmation of continued use since
Polymer Feed Advisor | Solids Handling | Net New | — | Solids Handling isn't a covered process area at all | Found an inverse relationship between polymer dosing speed and RST unit drive speed at a given feed %solids (14% more polymer speed ↔ 5-unit drop in RST drive at 1.5% feed solids); identified that polymer speed above 55% adds no further %TS benefit, and that an RST drive of 30 works best for 2–4.5% feed solids | Tune polymer use to the point of diminishing returns instead of over-dosing by habit — small dollar lever, but feeds directly into the disposal-cost lever below | Hull — delivered/documented (underlying analysis in Hull Milestone 5; 'Polymer Feed Advisor' is the GLWA case study's name for it) | Delivered in 2020 pilot — no confirmation of continued use since
Solids Disposal Advisor (hauling cost / truck count) | Solids Handling | Net New | — | Same — process area not covered | Tracks hauled sludge %TS against RST thickened-output %TS (found hauled solids run ~1.5% wetter than thickened output, likely measurement/residual-water issue); models that each 1% increase in hauled %TS cuts transport cost 13.6% (~$8,320/yr, ~17 fewer truckloads) by reducing hauled volume for the same dry-ton mass; also recommends renegotiating the disposal contract to weight cost by performance/flow rather than flat volume | Transportation is ~60% of the solids budget — this is the single biggest lever in solids management cost | Hull — delivered/documented (underlying analysis in Hull Milestone 5; 'Solids Disposal Advisor' is the GLWA case study's name for it) | Delivered in 2020 pilot — no confirmation of continued use since
Real-Time Mass Balance | Plant-wide | Net New | — | No mass balance calc in spec | Not elaborated on for Hull specifically — listed as a standing platform capability, presumably reconciling loading in vs. biosolids/effluent out across unit processes | Catch mis-calibrated meters or unaccounted losses, and support more defensible regulatory reporting | GLWA case study only — not confirmed for Hull | n/a — see 'Evidenced for Hull?' column
Automated Monthly I&I Report (RDII, RDII Ratio, GWI, Peaking Factor, Recovery Time, Rain Intensity) | Collection System / Reporting | Net New | — | No standardized reporting layer in spec — spec is live data only | Auto-generates a standard monthly table per node/WPCF: Localized Flow, RDII (rain-attributable flow above dry baseline), RDII Ratio (RDII as % of rainfall volume over the drainage area), GWI (rain-independent baseline infiltration, from dry-weather flow analysis), BSF, Peak Flow, Peaking Factor, Recovery Time, and Rain Intensity | Eliminates manual I&I report compilation and feeds MassDEP/NPDES regulatory reporting directly, on a consistent schedule | Hull — proposed (2025 upgrade scope), not yet delivered | n/a — see 'Evidenced for Hull?' column
Quarterly Seasonal Performance Summary (YoY) | Reporting | Net New | — | No periodic reporting deliverable in spec | Same node-level BSF/Infiltration/Inflow/I&I% plus storm-response stats (avg dry flow, peak storm flow, peaking factor, hours to peak), computed year-over-year vs. the same quarter prior year, plus a 'Decode Hydrograph' chart overlaying tide/rain/ADWF/actual flow, plus a pump-combo performance table for the quarter | Gives the Town an independent operational record separate from the contractor's own reporting, for capital planning and regulatory conversations — they explicitly caveat that findings should be paired with on-ground investigation, not taken as autonomous conclusions | Hull — delivered/documented (the Q4 2023 Summary doc IS this deliverable, already in production) | Confirmed active — shown in Q4 2023 report (Jan 2024) (this document IS that deliverable)
Cost/Savings Tracking ($/MG, O&M savings identified vs. realized, capital leverage) | Reporting | Net New | — | No savings/KPI tracking layer in spec | Baseline cost documented by unit process (energy/chemical/trucking $), tracked against a 'new baseline' post-optimization, with savings % computed per cost type and per process; applies a stated 13x capital-leverage rule ($1 of annual recurring O&M savings = $13 of capital investment capacity) | Translate operational savings into a capital-planning number leadership can act on — framed explicitly as a way to fund upgrades without raising rates or issuing debt | Hull — delivered/documented | Delivered in 2020 pilot — no confirmation of continued use since (the 2020 baseline/13x capital-leverage framework specifically isn't shown in the Q4 2023 report)
Training & Adoption Program (E-learning videos, champion-user model) | Program / Rollout | Net New | — | Not a dashboard data item — a rollout/adoption service Aquasight bundled in; flag for scoping, not build | Group training session for ops/maintenance/IT/utility staff, a recommended dedicated on-site monitor plus a 'champion' power user, short e-learning videos for onboarding new staff, and folding the platform into weekly O&M meetings | Their stated position: the platform only pays off if it's actually adopted day-to-day — this is change management, treated as a real deliverable | Hull — delivered/documented (training actually held Nov 18, 2020 per Milestone 6) | One-time completed activity (Nov 2020) — not an ongoing capability
AVA AI Assistant (Q&A, image analysis, engineering formulas) | Plant-wide | Net New | — | No AI assistant in spec; note Aquasight's own AVA doesn't connect to live client data either | A wastewater-domain assistant answering from general engineering knowledge/best practices (pump troubleshooting, F/M and SRT/MCRT calcs, LOTO/confined-space procedures, dosing calcs) and analyzing uploaded images (e.g., identifying a clogged pump from a photo). Explicitly does NOT query Hull's live data — it's a knowledge tool, not an operational query tool | On-demand engineering reference for staff, especially less-experienced operators, without pulling in an engineer for routine questions | Hull — proposed (2025 upgrade scope), not yet delivered | n/a — see 'Evidenced for Hull?' column
Pricing note: Aquasight doesn't itemize cost by feature/advisor anywhere in these docs — it's bundled. Known figures: 2019-2020 pilot buildout (transducers + install labor + cybersecurity) totaled $32,488.48 against a $50,000 budget; current ongoing cost is a single $8,000/yr platform license fee (Nov 2024 invoice), no feature-level breakdown. If per-feature cost matters for scoping, that's a question for Aquasight directly. | [7 empty] | n/a — see 'Evidenced for Hull?' column